GUIDE TO

BASIC

ELECTRICAL

INSPECTION

INTRODUCTION

Electricity is probably the most dangerous form of energy on the planet.  It does not alert the human senses, and because we are continually exposed to it, the risks can be extremely high.  To all intent and purpose, electricity appears harmless, and people become very blaséê about its use, but be under no illusion whatsoever, it is very very dangerous, and can be lethal if care is not taken.  We must give electricity 100% respect, because it has no respect for us - it will kill, given the opportunity.  It does not select its victim, and it has no respect for academic qualifications or competency.

Ironically it is probably the only form of energy that actually inspires curiosity.  A bare copper conductor begs the question, “is it live, or is it dead?” and it further beckons you to find out by touch, more often than not.  This is a fact because human being are very inquisitive specie, it is in their nature to find out.

It is essential to be constantly aware of the risk presented to use.  This will be achieved by diligent assessment.  Unfortunately risk assessment of electrical energy is not as straightforward as other forms of energy.  For example, most people who have had electric shocks, have survived, but that is not to say that they will survive the next electric shock.  The risk associated with electricity is very unpredictable, it can be compared to the “toss of a coin” and you take a chance.  To be sure that you are not caught in this trap the best advice is to stay clear of any live exposed conductor, or place something between you and any live part.  In addition, it always very wise to make sure that the electrical installation is in a safe and efficient state.

To achieve this, regular inspection or auditing is necessary.  This is the fundamental preparation of risk assessment, identification of the potential hazard.  Inspection is also the foundation for maintenance.  it is not difficult to carry out an electrical inspection ; you do not have to be Chartered Electrical Engineer to succeed in this undertaking.  The major instrument of inspection is your eyes, they assess the situation and the brain subsequently makes the judgement.  In other words “let your eyes do the work, and make judgement on what you see”.  This is the basis of inspection.

The object of the Guidance document is therefore to instruct the inspector, auditor or assessor, the simple method of electrical inspection and what to look for.  Also to supplement the observation, the guide also highlights the type of question that should be asked in order to reach a satisfying conclusion on the safety and integrity of the electrical installation.  Whatever you see, you will always formulate an opinion on whether it is right or wrong, and it is here where you begin.  In some cases, and installation may look wrong, but is could be perfectly safe.  There is no reason whatsoever why you cannot question it though.  If you feel concerned or uneasy about it, do not be afraid to ask or question it.  What is vitally important is that you should never ignore something which looks suspect, because this is tantamount to saying that it is acceptable ie.  Never ever condone a wrong because you are short of knowledge on the subject.

This Guide will provide the inspector/auditor with the tools to carry out the inspection, which of course is the prime weapon for risk assessment.  The Guide is written in Checklist form for ease, and it refers throughout to the legal requirement ie., the Electricity at Work Regulations 1989.

- General Inspection of the Installation (Regulations 4{1} & 4{2})

- Does it look as though it is installed properly? eg.,

- Are cables laid or run in an untidy manner?

- Are cables run near hot surfaces, or in areas where they can be damaged?

- Are cables terminated or glanded correctly?  Look for exposed cores and loose armouring.

- Are conduits and trunking firmly fixed?

- Are flexible cables being used to supply fixed equipment?

NOTE: You will get a “gut feeling” if an installation is not right, or is unsafe, by the general state of tidiness or upkeep.

- Is the installation, including connected equipment, adequately assembled and constructed to a safe standard? eg.,

- Is a flimsy piece of equipment being used in a harsh environment?  Examples of this are domestic appliances used in an industrial activity.

- Are flexible cables being used where conduit or trunking should be used?

- Are cables run without further efficient protection such as conduits or armouring?

- Check plugs and sockets for damage or overheating.

- Is the equipment and installation properly maintained to ensure that danger does not arise?  eg., look for,

- Missing bolts or fixing studs on covers, trunking and conduit box lids.

- Unfilled cable entry holes in electrical switchgear and control panels which permit objects, including fingers to penetrate.

- Broken covers and operating handles (particularly on isolators).

- Covers missing from trunking, conduit boxes which allow cables within to be exposed or hang out.

- Damaged trunking, conduit and insulation of cables.

- Open panel doors or dislodged lids on electrical enclosures which allow access to live parts within.

- Loose earth connections.  Do not be afraid to best this, as the earth conductor is normally dead and does not carry current.

- How is it being use?  eg.,

- Is the equipment being used in a dangerous state with broken covers, bare leads, damaged insulation?

- Is the equipment being given rough treatment by the operators?  Take special note of portable appliances, as these often fall into this category.

- Does the equipment and installation look safe in your opinion?

- Is conduit or trunking being used to stand on or support coats, bags etc?

- Exposed Conductors and Terminations (Regulation 7)

- Look for any exposed conductor or terminal and ask an electrician to prove whether it is live or dead.  Then ask him what voltage is applied to that conductor or terminal.

- If it is live check to see if it can be easily touched and whether access is unrestricted or not.  If it can be touched without difficulty, then it must be covered with insulating material, a screen or barrier, a shroud or they should be enclosed.

- Check carefully whether barriers, screens or division can be security erected or whether the conductor or terminal can be repositioned out of reach.

- Check to ensure that all cables entering plug tops or enclosures are securely gripped at their outer sheath by a cable grip such that inner cores are not exposed.  Check also the tightness of glands.

- Enclosures or barriers should have a minimum degree of protection against ingress of solid objects such as fingers, screwdrivers etc., not less than 12mm (IP2X - BSEN 60529, “Degree of Protection for Enclosures”).

- Are flexible conduits, or tubing, which contain electrical cables damaged or broken?  If so, they should be repaired immediately or replaced by say flexible braided composite cables.

- Do downshop bare overhead conductors, for overhead travelling cranes, pass windows, pipe flanges or equipment which has to be attended to from time to time?  If these conductors cannot be insulated, they should be covered with an insulated barrier or screen at the points where they pass windows, pipe flanges etc., to prevent persons carrying out the maintenance or attention coming into contact with them.  The voltage of these conductors are usually 415 volts AC.

- Joints and Connections (Regulation 10)

- Look for joints in flexible cables, particularly those which supply portable appliances, and see if they are insulated by PVC tape. To assess whether these joints meet the requirements of this regulation, it is necessary to satisfy oneself of the conductivity and insulation of the joint or connection.  The converse of conductivity is resistivity which means that if the joint has poor conductivity it will have a high resistivity and therefore the possibility of generating heat.  Unless you can see evidence of heat, it will be difficult to assess the conductivity.  In addition it can be difficult to assess the quality of insulation unless it can be tested.  Both of these prime requirements are not easy to establish.  What is easy, is whether the joint or connection can withstand the mechanical test.  To do this, simply switch off the supply to the cable and equipment, disconnect the plug, and pull on either side of the joint or connection, similar to pulling a Christmas cracker.  If the joint comes apart, then it is a prima facie breach of the regulation and of course it may be dangerous because one side of that joint will be live when the plug is inserted back into the supply.

- Note:  over 95% of joints fall into this category and are easy “meat” for prosecution.  Much more seriously however, they have been known to be the largest cause of accidents.  Whilst the regulation applies to all voltages, the greatest danger arises from systems operating at the mains, domestic voltage of 230 volts AC.

- Look out for ‘chocolate’ type connectors, plastic terminal strips or porcelain thimble type connectors, because all of these fall into this category.

- Check wrap around terminals fro security and tightness.  Be sure you isolate first before checking.  Also check for overheating of the terminal.

- Plugs are connectors, so check the condition of the plug ie., for overheating and damage.  Also check to see that there are no inner cores of the cable showing and that the plug securely fits into the socket outlet.

- Although the more established type joint should not give rise to problems, but always look for signs of dampness, corrosion or any possibility of electrolytic action.

- Isolation and Cutting off of Supply (Regulation 12)

- Check to make sure that every machine has a means of isolation and that this isolation is accessible.

- Check that every machine has a stop/start facility, and again check to see that it is readily accessible.  Also check to see if there is an accessible emergency stop button.  This type of button, often referred to as an Estop should be of the latch in type, have a mushroom head and coloured RED.

- Check to ensure that isolators are in good condition and can be operated without difficulty.  For example check for broken handles, impediment of operation or corrosion.

- Check that there is adequate isolation facility back at the main switchroom and at the various distribution points.

- Make sure that all isolation points are clearly marked for the circuits they control.  Identification is very important and should be looked for at every inspection.  This should also include identification of fuseways inside distribution boards, consumer units etc.

- Check to ensure all circuits have a means of switching off, eg., lighting and fan switches, socket outlets etc., make sure that these switches are in good working order an dare not broken.

- Earthing (Regulation 8)

NOTE  This is a specialist area of work and can only be correctly assessed by electrically competent personnel.  Nevertheless certain questions can be asked from general observation of the earthing arrangements.

- Check that all conductive parts (metal enclosures, pipes, radiators, taps etc). are bonded to earth.  If you cannot see the bonding, as the question.

- If the arty protective conductor (green/yellow or a green wire) or a bond is visible, check that the connections are tight.  They must be as tight as possible, because loose or slack connection s give a high resistance and could result in danger.  Also check to ensure that the connections are not corroded.

- Check the colour coding of the earth protective conductor.  This should be green/yellow.  Do not accept any other colour.

- Check the size of the earth protective conductors or bonding.  Small cables will not carry fault currents adequately and present dangerous voltages on exposed conductive parts when a fault occurs.  Ask the electrician or electrical engineer to check this out.

- Check to see if armouring, conduit or trunking is used for earthing.  If so check the tightness of glands, signs of corrosion, any damage to conduits or trunking and if there are any bonding straps.

- Ask the electrician or engineer if Earth Fault Loop Impedance Tests are carried out, and how often.  The earth Fault Loop Impedance will limit the fault current such that it may not blow the fuse or trip the circuit breaker.  Therefore the Earth Fault Loop Impedance should be so low that the fault current will be so high and will blow the fuse in the fastest possible time.  As the electrician or engineer what the value is of the Earth Fault Loop Impedance, and whether it will allow enough fault current to flow in the fault circuit to disrupt the protective fuse or circuit breaker in as fast a time as possible.

- Electrical protection (Regulation 11)

NOTE 1	Protective systems and their respective devices (eg., fuses and circuit breakers) are a complex subject and can only be assessed in detail by electrically competent persons.  Nevertheless some basic questions can be asked by the Inspector of Auditor, eg.,:-

- Is the circuit or system adequately protected to clear overloads, short circuits and earth faults in an acceptable time?

- Can you supply evidence of this eg,. by calculation or demonstration (current injection test)?

- What type of protective device is installed?  Is it a fuse, circuit breaker or relay?

- If it is a fuse, what type is it, rewirable, cartridge or HRC (high rupturing capacity)?

- Is the protection system graded to clear faults locally and not to cause shut downs of other circuits?  Show me how is achieved>

NOTE 2

- Inspect plug tops for silver paper, sawn off nails, hairclips and wire strapped across the fuse.

- Check the appliance or machine for its load rating and then assess the size of protective device which should be fitted.  This is done by selecting the device to be slighting in excess of the load rating/design current.  For example use the formula Watts = Volts x Amps.

- To prove this point lets take the following example.  A 1,000 watt electric fire operating at 230 volts will have a load/design current of 4.35 Amps and should be protected by a 5 amp fuse not a 3 amp or 13 Amp.  If a fault of 20 Amps were to occur, then the 5 Amp fuse would remove the fault in a half a second, whereas t could take up to 3 hours for the 13 Amp fuse to melt.

7.	Adverse Environments (Regulation 6)

- Firstly check the environment, is it:-

- Dusty

- Wet or damp (do they clean down using high pressure hoses)

- Corrosive

- Dirty

- Weather conditions

- High or low temperatures and/or pressures

- Potentially explosive/flammable atmospheres

NOTE:	Standard electrical equipment will be seriously affected by these conditions and danger will result.  Electrical equipment will have to be selected accordingly to suit the environment.  For example if a piece of equipment is installed outside and subjected to torrential rain then it should be at least “splash proof” (IPX4).  There are many British Standards which deal with the requirements for electrical equipment installed in adverse environments, and these should be consulted along with specialised advice.

- Check the type of installed equipment against the environment it has to work in, and advise accordingly using the following:-

- Dirty, dusty, wet or adverse weather		see BS: EN:60529 (IP Standard)

- Flammable/Explosive atmospheres		see BS:5501 and BS:5345

- Corrosion:  replace or clean down using a wire brush and repaint with an anti-corrosive paint.

- High temperature or pressure:  reposition the equipment or replace with equipment specially designed and manufactured for that environment.

- Check also the installation medium such as cables, conduits etc., it is better to use armoured cables or Mineral Insulated (MICC) types in most of these environments.

- Portable Tools

- Always check the supply voltage:

- NOTE 1	The safest voltage is the lowest practicable voltage.  Generally the recommended voltage is 110 volts AC supplied from a transformer with its mid point connected to earth (centre tapped to earth - CTE).  This arrangement limits the shock to earth voltage to 55 volts AC.  Where the degree of risk is much higher, for example in confined conducting spaces, the voltage should be much lower than this, ie., 50 volts from either an unearthed supply (electrical separation) or from a CTE supply to limit the shock voltage to 25 volts.

- NOTE 2	If the portable tool cannot be supplied from a 100 volt CTE supply, and has to be run at 230 volts or 415 volts AC then it should be given extra protection by a suitable RCD rated to trip at 30 milli amperes.

- NOTE 3	Double insulated or all insulated tools (Class 2) do not require an earth connection, it is therefore vitally important to ensure that the casing, cable insulation and plug are not damaged; and preferably this type of tool should be protected by a 30mA trip RCD.

- Check that all cables and entries are not damaged.

- Are there any taped joints similar to that mentioned earlier?  If so have then replaced by a better type joint or better still replace the cable.

- Check to see if the metal casing or other conductive parts of the tool are efficiently earth.  Seek the guidance of an electrician.

- Are the tools regularly inspected and tested?

- Check all plugs, fuses.  Cables and the conditions the tools are expected to work in.

- Work Activities (Regulations 4{3}, 13 and 14)

NOTE 	The law requires that all work done on electrical systems and equipment should be carried when the supply has been removed ie., DEAD, unless there is a very good and compelling reason for it to be done LIVE.

- The above must be established at the onset before agreeing to any work when the supply is still connected.

- Whatever the manner in which the work is to be done, you must satisfy yourself that the person undertaking the work is sufficiently COMPETENT for the task at hand (refer to the Section on Competency).

- WORKING ON DEAD EQUIPMENT (Regulation 13)

- Do they have a safe system of work, written down, which ensures that when the supply has been removed for work to be done on dead conductors, it remains off until the work is completed?  Also ask them to demonstrate the discipline behind this system of work (if they have one).

- Check the following:

- Are the circuits to be worked on, clearly identified?

- Can they be ISOLATED and LOCKED OFF?

- Are unique locks and keys used?

- Does the person doing the work carry his own key at all times?

- Does the person doing the work prove the circuit DEAD before commencement?

- Are his test instruments suitable for the task, and are they in good working order?

- Do they have proper Warning Notices, and are they always used?

- Do they have personal/portable earthing equipment?  (this is optional).

- If they have a different system to the one just described, examine it carefully; it may be quite acceptable, on the other hand it may not.  The above one is the one normally recommended, but that is not to say others cannot offer better safety and security, so check it out carefully.

- Ask members of the electrical department to describe in detail their system of work.  This is a good way of proving whether they know it or not.

- Ask members of the electrical department to show you their test equipment.

- LIVE WORKING (Regulation 14)

- Do they have a policy for LIVE working?

- Ask to see their risk assessment for the work involved.

- Check on the precautions they are adopting for the risks involved in the work.

- Check to see if the conductors can be insulated.

- Examine the competency of the persons who will do the work.  Find out if the person doing the work is fully conversant with the nature of the work and the equipment and systems involved.

- Does he have all the information and drawings available to him?

- Does he require Supervision?  Is this readily available?

- Do they have a WORK PLAN?  Examine it carefully, and see if they highlight the dangers and what precautions they are to put into operation to safeguard the workmen.

- Have they supplied all the required suitable protective equipment such as insulated tools, rubber mats, temporary or permanent screens, barriers, shrouding, protective clothing and proper test equipment?

- Does the person carrying out the work have adequate working space, access and lighting?

- Have all the necessary precautions been taken to allow the person to work alone, or doe she need Accompaniment?  Can they provide Accompaniment?

- If Accompaniment is required, would the Accompanying person know what to do in an emergency?  Has this person had any training on Accompaniment, or at least has he been given any instruction?

- Have their persons involved in live work, including Accompaniment, have any First Aid training?

- If they have any safety documents for live work eg., Permits to do Live Work, examine them and check to see if they are adhered to.

- Competency (Regulation 16)

NOTE	Competency is the sole responsibility of the Employer and his Management to satisfy themselves that, at all times, persons engaged in electrical work have been adequately trained and have sufficient experience to carry out the work both competency, and more importantly, safely.  In addition they must ensure that those persons are fully familiar with the equipment and systems they are expected to work on.

- Ask to see the training records and check on the syllabus of training and compare it with the work involved.

- Check the “ON THE JOB TRAINING” programme and how the individual’s performance is monitored.

- Enquire as to how the level of competence is arrive at and who makes the ultimate assessment.

- Ask the individual concerned the following questions:-

- Does he/she know where the dangers are?

- Does he/she know how to avoid these dangers?

- Is he/she happy with the training they have received?

- Is he/she confident that he/she can do the job without risk to him/herself and others?

- Is he/she satisfied with his/her own particular technical knowledge and experience associated with the work involved?  ask what do they think should be done to bring them up to the required level.

- Is he/she provided with all the necessary information and instruction to allow him/her to do the work safely.

- Is sufficient Supervision provided.

- Does he/she require any further safety training?

- Do the Company monitor their employees regularly?

- Do the Company know where to go to improve the competency performance of their personnel?

- Is the Company familiar with their legal obligations in relation to competency?

- Personal Protective Equipment (Regulation 4{4})

Insulated Tools

- Do electricians have insulated tools?

- Inspect them and ask, or enquire, as to whether they comply with IEC 900 (Handtools for Live Working up to 1,000 volts AC or 1500 volts DC).

- Are the insulated tools regularly inspected, and how often?  They should be examined at least yearly.

- Insulated Mats

- Are insulated mats (to BS 921) provided in front of switchboards (particularly LV switchboards)?

- Are these mats regularly inspected, and how often?

- Are the mats always kept in place in front of the switchboards?  Check!

- How often are rubber mats re-tested?  They should be withdrawn for test every 5 years.

- Check to make sure that the rubber mat extends beyond the switchboard.

- Rubber Gloves

- Do they provide rubber gloves?

- Are these to BS 697?  Ask them to verify.

- How do they contain gloves not in use?  They should be kept, unfolded, in a plastic bag which contains Talcum Powder.

- Check to see how the gloves are cleaned.  They should be washed, dried and dusted with Talcum Powder (petroleum spirit must not be used).

- NOTE:	Gloves in regular use should be replaced every 6 months.  Those which are not in regular use shall be re-tested every year.

- Barriers and Test Equipment

- Are insulated screens, division and barriers etc., available to electricians when they are expected to work near live conductors?

- Is the test equipment supplied to, or used by, electricians suitable and safe; and do the test prods satisfy HSE Guidance Note GS38?

- Clearance, Access and Lighting (Regulation 15)

Clearance and Access

- Check the clearance space in front of switchboards and other electrical equipment where work is expected to be carried out.

- NOTE:	The Electricity at Work Regulations 1989 do not give distances, but a good guide is provided by their predecessors, the Electricity (Factories Act) Special Regulations 1908 and 1944 and should be considered.  These regulations ask for 3’0” clearance for voltages up to 650 volts and 3’6” for voltages beyond that.

- Are areas in front of switchboards fouled by storage materials or other foreign bodies such that access to isolation and switching points is severely impeded?

- Are switchrooms and/or sub-stations being used as storerooms?

- Ensure that access, free from danger, is provided at every item of electrical equipment, and that sufficient working space is available for persons to work.

- Lighting

- Is sufficient and adequate lighting provided where electrical work, including the operation of switches and isolators is normally carried out.

- Check that sufficient and adequate lighting is provided in sub-stations and switchrooms.

NOTE	HSE have a good Guidance Note out on “Lighting at Work”, HS/G38.

- Maintenance (Regulation 4{2})

- Do they have any form of maintenance in operation, eg., inspection/auditing, planned or scheduled, or simply breakdown maintenance?

- How regular is this done, and do they keep records?  (Check the records thoroughly).

- Is action taken?

- Is the maintenance effective in your opinion?

- Temporary Installations and Flexible Cables

NOTE 1	Quite a number of temporary installations are not really temporary at all.  They generally stay that way for long periods, sometimes forever.  Using temporary supplies is a lazy and cheap way of putting equipment into use.  Because of the very nature in which the installation is executed, it is extremely vulnerable and is often subjected to damage.  The result being that danger is ever present to those working with temporary supplies.

The fact that it is “temporary” does not mean that it has any sort of exemption under law.  They are most certainly NOT exempt.  Every electrical installation must comply with the 1989 Regulations irrespective of their duration of operation.  The law will come down heavily on temporary installations because the risk of personal injury is more likely to happen.

NOTE 2	Always check the voltage used for temporary installations.  If they are supplied at mains 230 volts AC, or above eg., 3 phase 415 volts AC, then they should be protected by an RCD designed to trip at 30mA preferably in 40 milli seconds.

NOTE 3	Welding cables are flexible and also temporary, and therefore came into this category.

- Ask the question “Is the equipment in its final position”?

- If the answer is YES, then request that it should be installed in a permanent manner using conduit, trunking or armoured cables.

- If the answer is NO, then ask how long it is to remain in that temporary condition.  You now have a date, for which you can return, to check that the temporary installation has ended.

- Examine the way the equipment is erected.  Check to ensure that it cannot be knocked over, or in a position to be damaged.

- Ensure that the equipment is well constructed and does not have any exposed live conductors.

- Ensure that access to live parts is not normally possible.  Access should only be limited to electrically competent persons.

- Are flexible cables laid across the floor, or in positions where they can be easily damaged.  Have them re-routed into safe areas.

- Check also that flexible cables are not lying in water, oil, chemicals or within combustible materials.

- Check the condition of cables, any damage should either be repaired using a plug and socket or completely replaced with a new cable.

- Cable should always be gripped at their outer sheath by a cord grip within the plug or appliance/equipment.

- Flexible cables should be kept as short as possible, preferably no longer than 2 metres.

- Avoid the use of extension leads wherever possible.  If they have to be used, they ought to be in operation for short periods only, and run in a tidy fashion out of harm’s way.

- On no account accept single core leads as a supply to equipment.  All flexible cables should be of the composite type, complete with an outer sheath.

- Flexible cables should be flexible, and not stiff PVC/PVC flat twin and earth types.

- Look carefully at the method of supply, eg.,:-

- Do not accept multi-way adapters.

- Do not accept two or more cables in one plug top.

- Do not accept conductors held in socket outlets with matchsticks.

- Check that the installation of isolators, switches, fuseboards etc., are securely fixed to walls, stanchions or other firm support structures.  Do not accept  such supply equipment if it is lying on the ground.

- Always ensure that the supply points can be easily isolated or switched off without any obstruction.

FOOTNOTE	Never be afraid to ask if you have any doubt; and get to know your local Enforcement Officer.  He/She will be glad to provide all the help you need.